## Storage Logs
Triton S-Series Submersible Maintenance Form V454
Serial Number
Pump Model
Project Name
Delivery Date
Storage Maintenance Requirements & Log
If equipment is to be stored for longer than two weeks, take the following action:
1. Coat exposed steel with a light layer of grease or Cosmoline to protect the equipment from corrosion.
2. Rotate the motor 1-1/4 turn once each week to keep the bearings from sitting in one position for extended periods of time.
3. Avoid storing rotating equipment near other vibrating equipment. The vibrations can damage the ball bearings and result in premature failure once the equipment is started up.
4. Store rotating equipment in a clean, dry, heated area away from areas where it could be damaged from impact, smoke, dirt, vibration, corrosive fumes or liquids, or from condensation inside the motor or pump. It may be helpful to cover equipment with plastic.
5. The pump column and bearing housing are assembled as an oil-filled assembly so that the seal and lower bearings are covered in oil. To avoid bearing corrosion these housings should be kept filled with ISO Grade 46 hydraulic oil to normal levels. (Note that the top bearing is grease lubricated. An air gap should be left below the top two bearings. Do not over fill.)
Monthly Storage Maintenance
| Rotate motor 1 -1/4 turn | Name and Date
Month 1 | Yes_____ No______
Month 2 | Yes_____ No______
Month 3 | Yes_____ No______
Month 4 | Yes_____ No______
Month 5 | Yes_____ No______
Month 6 | Yes_____ No______
Month 7 | Yes_____ No______
Month 8 | Yes_____ No______
Month 9 | Yes_____ No______
Month 10 | Yes_____ No______
Month 11 | Yes_____ No______
Month 12 | Yes_____ No______

## Monthly Maintenance
Triton S-Series Submersible Maintenance Form V454
Serial Number
Pump Model
Project Name
Start-up Date
Monthly Operational Maintenance
| Amperage Draw | Is oil contaminated or milky? | Name and Date
Month 1 |  | Yes_____ No______
Month 2 |  | Yes_____ No______
Month 3 |  | Yes_____ No______
Month 4 |  | Yes_____ No______
Month 5 |  | Yes_____ No______
Month 6 |  | Yes_____ No______
Month 7 |  | Yes_____ No______
Month 8 |  | Yes_____ No______
Month 9 |  | Yes_____ No______
Month 10 |  | Yes_____ No______
Month 11 |  | Yes_____ No______
Month 12 |  | Yes_____ No______

## Annual Maintenance
Triton S-Series Submersible Maintenance Form V454
Serial Number
Pump Model
Project Name
Start-up Date
Annual Operational Maintenance
Annual maintenance is to be performed IN ADDITION TO monthly maintenance
Pump | Pump removed from pit and inspected for wear or damage? | Clearances checked between impeller and cutter bar? | Smooth rotation and no axial play of shaft? | Name and Date
| Yes_____ No______ | Yes_____ No______ | Yes_____ No______
| Is oil leaking across seal faces? | Pump casing or adapter bracket worn? | Loose, corroded or worn hardware? | Name and Date
| Yes_____ No______ | Yes_____ No______ | Yes_____ No______