## Storage Logs
Turbo Agitiator Form 328
Serial Number
Pump Model
Project Name
Delivery Date
Storage Maintenance Requirements & Log
If equipment is to be stored for longer than two weeks, take the following action:
1. Coat exposed steel with a light layer of grease or Cosmoline to protect the equipment from corrosion.
2. Rotate the motor 1-1/4 turn once each month to keep the bearings from sitting in one position for extended periods of time.
3. Avoid storing rotating equipment near other vibrating equipment. The vibrations can damage the ball bearings and result in premature failure once the equipment is started up.
4. Store rotating equipment in a clean, dry, heated area away from areas where it could be damaged from impact, smoke, dirt, vibration, corrosive fumes or liquids, or from condensation inside the motor or pump. It may be helpful to cover equipment with plastic.
5. The turbo column and bearing housing are assembled as an oil-filled assembly so that the seal and lower bearings are covered in oil. To avoid bearing corrosion these housings should be kept filled with ISO Grade 46 hydraulic oil to normal levels. (Note that the top bearing is grease lubricated. An air gap should be left below the top two bearings. Do not over fill.)
Monthly Storage Maintenance
| Rotate motor 1 -1/4 turn | Name and Date
Month 1 | Yes_____ No______
Month 2 | Yes_____ No______
Month 3 | Yes_____ No______
Month 4 | Yes_____ No______
Month 5 | Yes_____ No______
Month 6 | Yes_____ No______
Month 7 | Yes_____ No______
Month 8 | Yes_____ No______
Month 9 | Yes_____ No______
Month 10 | Yes_____ No______
Month 11 | Yes_____ No______
Month 12 | Yes_____ No______

## Monthly Maintenance
Turbo Agitiator Form 328
Pump Model
Project Name
Start-up Date
Monthly Operational Maintenance
| Amperage Draw | Name and Date
Month 1
Month 2
Month 3
Month 4
Month 5
Month 6
Month 7
Month 8
Month 9
Month 10
Month 11
Month 12

## Quarterly Maintenance
Turbo Agitiator Form 328
Serial Number
Pump Model
Project Name
Start-up Date
Quarterly Operational Maintenance
Quarterly Maintenance is to be performed IN ADDITION TO monthly maintenance
Motor | Drain plugged? | Cooling fins cleaned? | Loose or corroded hardware? | Damaged wiring or conduit? | Name and Date
Quarter 1 | Yes_____ No______ | Yes_____ No______ | Yes_____ No______ | Yes_____ No______
Quarter 2 | Yes_____ No______ | Yes_____ No______ | Yes_____ No______ | Yes_____ No______
Quarter 3 | Yes_____ No______ | Yes_____ No______ | Yes_____ No______ | Yes_____ No______
Quarter 4 | Yes_____ No______ | Yes_____ No______ | Yes_____ No______ | Yes_____ No______
Pump | Loose or corroded hardware? | Oil clean and at the proper level? | Pump operating smoothly and without vibration? |  | Name and Date
Quarter 1 | Yes_____ No______ | Yes_____ No______ | Yes_____ No______
Quarter 2 | Yes_____ No______ | Yes_____ No______ | Yes_____ No______
Quarter 3 | Yes_____ No______ | Yes_____ No______ | Yes_____ No______
Quarter 4 | Yes_____ No______ | Yes_____ No______ | Yes_____ No______

## Semi-Annual & Annual Maint
Turbo Agitiator Form 328
Serial Number
Pump Model
Project Name
Start-up Date
Semi-Annual Operational Maintenance
Semi-annual maintenance is to be performed IN ADDITION TO monthly maintenance and quarterly maintenance
Motor Bearings Greased? |  |  |  | Name and Date
Yes_____ No______
Yes_____ No______
Annual Operational Maintenance
Annual maintenance is to be performed IN ADDITION TO monthly maintenance and quarterly maintenance
Turbo removed from pit and inspected for wear or damage? | Clearances checked between propeller and cutter? | Smooth rotation and no axial play of shaft? | Oil leaking across seal faces into elbow? | Name and Date
Yes_____ No______ | Yes_____ No______ | Yes_____ No______ | Yes_____ No______